RUG9  SPECIFICATION

LOGIC FAMILY

All low power CMOS

MICROPROCESSOR

32-bit 68331, 16 Mhz, 16 bit data bus, 24 bit address bus

MEMORY

RAM-256 Kbytes battery backed low power static RAM

FLASH-512 Kbytes

Battery Backup-Lithium coin cell backs up RAM & realtime clock/calendar min 2 years

MEMORY CARTRIDGE

4 Mbyte to 10 Mbyte  removable Sandisk Flash cartridge

I/O EXPANSION

First card cage can have any I/O, modems, FlashDisk, sleep board, etc., up to 8 cards plus CPU.  Up to 7 card cages attach with ribbon cables, can hold I/O up to 64 ch per cage.

DISPLAY

20 line X 40 char (320 by 240 dot)  backlit graphic LCD, 6 in diag. detachable from card cage.

Text- All std ASCII chars plus special graphic chars

Trends-Up to 10 traces per page; pages incorp into user defined text pages, as many as will fit in RAM.  User defined scale grid.

Bargraphs-Up to 20 hor bars/display page to show analog values

KEYBOARD

16 key sealed tactile membrane with interrupt scanning

REALTIME CLOCK/CALENDAR

Battery backed clock/calendar 0.005% crystal accuracy, Y2K

SPEECH SYNTHESIZER

8 Khz sampling record & playback.  Up to 256 messages in 12 minutes total storage.

OPERATION SECURITY

Watchdog Timer-Hardware timer resets unit 0.5 sec. after interrupt fail.  Cannot be disabled.

Telemetry Watchdog-Resets rcv buffer if no character received within 1 sec.

Brownout Detector-Halts process if  logic voltage falls below 4.75 V, restarts when voltage rises to 5 V

AUTOBOOTING

Auto startup on power application

I/O SURGE PROTECTION

All I/O is optically isolated, meets IEEE surge protection rqmts.

ANALOG INPUTS

8 ch per board, 12 bit res., successive approx, optically isolated, 4-20 ma or 0-5 v.  Factory calibrated.

ANALOG OUTPUTS

4 chan per board, 12 bit resolution, optically isolated.

DIGITAL INPUTS

Status- 8 chan/board, optically isolated, 120VAC or 24 VDC compatible.

Pulse Counting-all DI channels in first card cage count 128 PPS

Pulse Duration Detecting-all DI in first card cage can convert pulses to analog with 4ms resolution

DIGITAL OUTPUTS

8 ch per board, 3  amp relays

Pulse Duration Outputs-Base relays can generate PWM or one shot signals with 4 ms res.

SERIAL PORTS

Up to 8 RS232/modem ports or 8 dual RS232/printer ports in base card cage

MODBUS Protocol

Std RTU master or slave protocol on any port except programming port

MODEM

Bell 103/212 standard

Radio Interface

4-wire audio, adj. gain, xformer isolated, isolated key line.  Low tones mode for splinter chan

Phone Interface

2 wire audio adjustable gain, transformer isolated

Autodialing

On/off hook relay, touchtone generate

Autoanswering

On/off hook relay and ring detector

Touchtone Detection

Standard tones on speech board

Communications

Background CRC gen/decode, variable length messages, user defined message lengths.  Can combine status, int, float, and double precision int in any message.

# Eavesdrop Mode

Any RTU can accept data passing between any other stations

Peer to Peer

Full RTU to RTU or RTU to master or master to RTU messaging

Store and Forward

Initiating station sets path through up to 3 intermediary stations

Address Range

1 to 255

PRINTER /RS232 PORT BOARD

Standard Centronics compatible  parallel port, dual RS232 ports.  Selectable RS485 port 1; SDI-12  port 2.

# FLASH CARTRIDGE INTERFACE

Board accepts 4 M to 10 Mbyte removable Compact Flash cartridge.  Dumps logged data in ASCII

POWER INTERFACE

12 VAC/15 VDC +/-20%, 130 ma. to 2.5 amps max, resettable fuse.

Loop Supply

Isolated, regulated 24 VDC +/- 5%, fused, 160 ma.

Battery Charger

160 ma., reverse protected, fused.

I/O CONNECTIONS

All I/O uses removable rising cage screw headers in banks of up to 12 each, 14 ga wire

SOFTWARE

Storage-operating system and all user config. and programming stored in nonvolatile flash memory.  Flash loader stored in flash  protected boot block.

Security-parameter voting and memory integrity test on boot up, CRC gen/detect on serial ports

Scanning-Built in software scans all I/O, ports, timers, realtime clock

PROGRAMMING

Modules-applications use precompiled modules resident in flash memory where programmer  interconnects modules and sets properties using supplied Win95/98/NT program.  No programming rqd for  most applications.

LADDER LOGIC

Ladder logic is built in to the WIN95/98/NT configuration program to handle misc controls

VARIABLES

Supports 32 bit integer, floating point, boolean, strings, arrays

ERROR MESSAGES

Configuration program handles all setup errors.  Run time software is self protecting... no run time errors.

ENCLOSURE

16 ga. Steel, blue powder coat 9 slot card cage with detachable display/keyboard module

Cage: 9.75 X 4.6 X 4.1 in.

DSP:  8.6 X 4.8  X 0.75 in

TEMPERATURE RANGE

-40 to +85 deg. C logic

-20 to +60 C LCD display

DOCUMENTATION

300 page bound manual

WARRANTY

1 year std limited warranty

REPAIR

Nominal 24 hr turnaround

RUGID COMPUTER,  6305 Elizan Dr. NW,  Olympia, WA 98502   (360) 866-4492   FAX (360) 866-8074